Lead and Copper Sample Site Selection Form

The Lead and Copper Rule, 40 CFR 141.80-93 and incorporated by reference in IDAPA 58.01.08.350, requires all community and non-transient, noncommunity water systems to sample at locations that may be susceptible to high lead or copper concentrations. 40 CFR 141.86 establishes a tiering system for prioritizing sampling sites. Water systems must develop a lead service line inventory prior to completing this form and identifying sample sites. This form defines the monitoring requirements, tiering system for prioritizing samples sites, and includes a site selection location table for submittal to the Idaho Department of Environmental Quality. This form is intended to help with site selection, but you are not required to use this form if you can otherwise certify the necessary information required under 40 CFR 141.86.

| Table 1: Lead and Copper Tap Monitoring |  |  |
| --- | --- | --- |
| System Size | Minimum Number of Tap Sample Sites (40 CFR 141.86(c)) |  |
|  | Standard Monitoring | Reduced Monitoring |
| >100,000 | 100 | 50 |
| 10,001 to 100,000 | 60 | 30 |
| 3,301 to 10,000 | 40 | 20 |
| 501 to 3,300 | 20 | 10 |
| 101 to 500 | 10 | 5 |
| < 100 | 5 | 5 |

| Table 2: Tiering Classification |  |  |
| --- | --- | --- |
| Tier | Community Water System | Non-Transient Non-Community Water System |
| Tier 1 | Single-family structures that are served by a lead service line or Multiple-family structures served by lead service line that comprise at least 20% of the structures served by the water system (40 CFR 141.86(a)(3)). | Sites served by a lead service line (40 CFR 141.86(a)(8)). |
| Tier 2 | Multiple-family residences or buildings that are served by a lead service line (40 CFR 141.86(a)(4)). | N/A |
| Tier 3 | Single-family residences with galvanized lines downstream of a lead service line, lead gooseneck, pigtail or connector (currently or in the past) (40 CFR 141.86(a)(5)). | Samples sites that contain galvanized service lines that are downstream of a lead service line, lead gooseneck, pigtail, or connector (40 CFR 141.86(a)(9)). |
| Tier 4 | Single-family residences with interior copper piping with lead solder installed before 1989 (40 CFR 141.86(a)(6)). | N/A |
| Tier 5 | Single-family or multiple family residences or buildings that are representative of sites throughout the distribution system. System may use non-residential buildings that are representative of sites throughout the distribution system only if there are an insufficient number of single-family or multiple family residential Tier 5 sites available. A representative site is a site in which the plumbing materials used at that site would be commonly found at other sites served by the water system (40 CFR 141.86(a)(7)). | Sample sites that are representative of sites throughout the distribution system. A representative site is a site in which the plumbing materials used at that site would be commonly found at other sites served by the water system (40 CFR 141.86(a)(10)). |

Service Line Inventory Results and Sites Selection Form

| PWS ID: Click or tap here to enter text. | PWS Name: Click or tap here to enter text. |
| --- | --- |
| Population: Click or tap here to enter text. | Total number of sample sites: Click or tap here to enter text. *Based on minimum number of tap sample sites from Table 1. |
| Name: Click or tap here to enter text. | Title: Click or tap here to enter text. |
| Date: Click or tap to enter a date. | System Type: Choose an item. |

Sample Site Summary

| Table 3: Number of Sample Sites Per Tier Directions: - Refer to Table 1 to determine the required number of lead and copper samples your system must collect. - Using the addresses from your system's lead service line inventory and the criteria provided in Table 2 of this form, fill in the number of samples below for each tier until the minimum number of tap sample sites is met. Note: Only Tier 1 and LSL sites should be selected for monitoring. If you cannot locate enough Tier 1 sites to meet the minimum sample site requirements, then Tier 2 sites may be selected. If you cannot locate enough Tier 2 sites, then Tier 3 sites may be selected. If you cannot locate enough Tier 3 sites, then Tier 4 sites may be selected. If you cannot locate enough Tier 4 sites, then Tier 5 sites may be selected. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Single Family Residence served by a lead service line Or Multiple-family structures served by lead service line that comprise at least 20% of the structures served by the water system | Multi-family residence or buildings served by a lead service line | Single-family residences with galvanized lines downstream of a lead service line, lead gooseneck, pigtail or connector (currently or in the past). | Single-family residences with interior copper piping with lead solder installed before 1989. | Single-family or multi-family residences or buildings with service line and interior piping materials representative of the distribution system. (Refer to Tier 5 in Table 2 for the definition of representative sites). |
| Tier 1 | Tier 2 | Tier 3 | Tier 4 | Tier 5 |
| Table 4: Sampling Site Addresses Directions: Please use Table 4 or attach the lead service line inventory to provide the addresses of the selected sampling sites. This form will expand when used electronically. |  |  |  |  |
| Tier 1 sample sites: Click or tap here to enter text. |  |  |  |  |
| Tier 2 sample sites: Click or tap here to enter text. |  |  |  |  |
| Tier 3 sample sites: Click or tap here to enter text. |  |  |  |  |
| Tier 4 sample sites: Click or tap here to enter text. |  |  |  |  |
| Tier 5 sample sites: Click or tap here to enter text. |  |  |  |  |

Water Quality Parameter Sites

All Community and Non-Transient Non-Community systems are required to identify Water Quality Parameter (WQP) sites. WQP sampling is in addition to lead and copper sampling.

Systems required to take Water Quality Parameters

- All large systems.

- Small- and medium systems that exceed the lead or copper action level.

- Small and medium systems with corrosion control treatment that exceed the lead trigger level.

Instructions

- Refer to Table A: Find the minimum number of Water Quality Parameter (WQP) sites your system needs to sample from.

| Table A. Minimum Lead and Copper WQP Tap Sample Sites (40 CFR 141.87(2)) |  |  |
| --- | --- | --- |
| System Size (number people served) | Standard Monitoring | Reduced Monitoring |
| >100,000 | 25 | 10 |
| 10,000 – 100,000 | 10 | 7 |
| 3,000 – 10,000 | 3 | 3 |
| 501 – 3,300 | 2 | 2 |
| 101 – 500 | 1 | 1 |
| < 100 | 1 | 1 |

- Record Information in Table B: Write down the addresses for each WQP site necessary to meet the minimum site requirements outlined in Table A.

| Table B. Addresses of sample sites |  |
| --- | --- |
|  | 14. |
|  | 15. |
|  | 16. |
|  | 17. |
|  | 18. |
|  | 19. |
|  | 20. |
|  | 21. |
|  | 22. |
|  | 23. |
|  | 24. |
|  | 25. |